## PointSummaryReport_2019_08_19__ (hidden)
PC Date and Time | 08/19/2019 08:34:58
Device Name | Device ID | Equipment Profile | Device Type | Point Type | Point Instance | Point Name | Value | change to | Unit | Reference | Out of Service | Reliability | Active Priority | Priority Owner | Relinquish Default | State Text | Minimum Value | Maximum Value | Value Triggered TGP2 Program | Run Program on False-->True | Run Program on True-->False | Run program on Low Limit | Run program on High Limit | Run program on fault | Run program on return to normal | Polarity | Offset | Multiplier | Filter Weight | Reference Type | Minimum On Times | Minimum Off Times | Update Interval | Update Priority | Alarm Table | Alarm Value | Feedback Reference | Low Limit | High Limit | Deadband | Event Time Delay | Heartbeat Interval | Outside limits/ In Alarm Notification | When Failed Notification | Return to Normal Notification | Notification Class | Notify Type | Alarm Lockout | Lockout References | Low Limit[EEO] | High Limit[EEO] | Deadband[EEO] | Event Time Delay[EEO] | Outside limits[EEO] | When Failed Notification [EEO] | Return to Normal Notification [EEO] | Notification Class [EEO] | Notify Type [EEO] | Alarm Lockout [EEO] | Lockout References [EEO]
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 1 | S/Air Temperature Local | 45 |  | °F | UI1.analogValue | FALSE | Unreliable Other |  |  |  |  | -58 | 200 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 2 | O/Air Temperature Local | 45 |  | °F | UI2.analogValue | FALSE | Unreliable Other |  |  |  |  | -58 | 200 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 3 | Outdoor Air RH Local | -24.92 |  | % | UI3.analogValue | FALSE | Under Range |  |  |  |  | 0 | 100 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 4 | Pressure Input (optional) | -0.331 |  | in(H2O) | P1.analogValue | FALSE | Under Range |  |  |  |  | 0 | 5 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 5 | Space RH (Optional) | 30 |  | % | UI8.analogValue | TRUE | No Fault Detected |  |  |  |  | 0 | 100 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 6 | Space Temp (Optional) | 0 |  | °F | AO2/UI10.analogValue | TRUE | No Fault Detected |  |  |  |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AI | 7 | Space Sp Dial (Optional) | 0 |  | °F | AO3/UI11.analogValue | TRUE | No Fault Detected |  |  |  |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 | 1 | 0 |  |  |  | 0:00 |  |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AO | 1 | Heating Control Signal | -10 |  | % | AO1/UI09.analogValue | FALSE | Unreliable Other | 9 | BurnerControlDFV48aBacNet | 25 |  | 0 | 100 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 |  | 0 |  |  |  | 0:00 | 16 |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AO | 3 | OA/RA Damper | 0 |  | % | AO6/UI14.analogValue | FALSE | No Fault Detected | Default |  | 0 |  | -150 | 150 |  |  |  | FALSE | FALSE | FALSE | FALSE |  | 0 |  | 0 |  |  |  | 0:00 | 16 |  |  |  | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 1 | Space Temp Setpt (BAS) | 0 |  | °F |  | TRUE | No Fault Detected | Default |  | 0 |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 2 | Occ Space Cooling SP | 78 |  | °F |  | FALSE | No Fault Detected | Default |  | 78 |  | 65 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 3 | Eff Occ Cool SP | 78 |  | °F |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 0 |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 4 | Eff Occ Heat SP | 74 |  | °F |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 0 |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 5 | Occ Space Htg SP Offset | 4 |  | °F |  | FALSE | No Fault Detected | Default |  | 4 |  | 0 | 6 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 6 | HGRH Control Deadband | 4 |  | °F |  | FALSE | No Fault Detected | Default |  | 4 |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 7 | Active S/Air Heat SP | 72 |  | °F |  | FALSE | No Fault Detected | 9 | SupplyAirSetpointDFandIFV48aBacNet | 60 |  | 40 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 8 | S/Air Low Temp Cutoff | 34 |  | °F |  | FALSE | No Fault Detected | Default |  | 34 |  | 34 | 50 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 9 | S/Air High Temp Cutoff | 125 |  | °F |  | FALSE | No Fault Detected | Default |  | 125 |  | 125 | 125 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 10 | O/Air Enthalpy | 10.8 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 0 |  | -98.9 | 98.9 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 11 | Occ Space RH SP | 60 |  | % |  | FALSE | No Fault Detected | Default |  | 60 |  | -150 | 150 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 12 | Occ S/Air Heating SP | 72 |  | °F |  | FALSE | No Fault Detected | Default |  | 72 |  | 40 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 13 | Space Cooling SP | 78 |  | °F |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 70 |  | 65 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 14 | Active Space Heating SP | 74 |  | °F |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 72 |  | 40 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 15 | Y1 - O/A Dehumid Enable | 28 |  | BTU/lb |  | FALSE | No Fault Detected | Default |  | 28 |  | 23 | 29 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 16 | Y2 - O/A Dehumid Enable | 36 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 34 |  | 29 | 36 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 17 | Unocc Space Heating SP | 50 |  | °F |  | FALSE | No Fault Detected | Default |  | 50 |  | 50 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 18 | Unocc Space Cooling SP | 85 |  | °F |  | FALSE | No Fault Detected | Default |  | 85 |  | 75 | 90 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 19 | Unocc Space RH SP | 65 |  | % |  | FALSE | No Fault Detected | Default |  | 65 |  | 55 | 65 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 20 | O/Air Heating Enable SP | 50 |  | °F |  | FALSE | No Fault Detected | Default |  | 50 |  | 40 | 90 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 21 | Y1 - O/A Cooling Enable | 78 |  | °F |  | FALSE | No Fault Detected | Default |  | 78 |  | 55 | 85 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 22 | Y1- Active 0A Dehumid SP | 28 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 0 |  | -98.9 | 98.9 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 23 | Y2- Active 0A Dehumid SP | 36 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | 0 |  | -98.9 | 98.9 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 24 | Unocc S/Air Heating SP | 80 |  | °F |  | FALSE | No Fault Detected | Default |  | 80 |  | 40 | 90 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 25 | Htg Failure Temp Deadbnd | 1.8 |  | °F |  | FALSE | No Fault Detected | Default |  | 1.8 |  | 0 | 10 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 26 | Htg Failure TD | 5 |  |  |  | FALSE | No Fault Detected | Default |  | 5 |  | 0 | 10 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 27 | Active O/A Dehum Y1 Enab | 28 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | EnthalpySetpointResetDFandIFV48aBacnet | 26 |  | 10 | 30 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 28 | Active O/A Dehum Y2 Enab | 36 |  | BTU/lb |  | FALSE | No Fault Detected | 9 | EnthalpySetpointResetDFandIFV48aBacnet | 29 |  | 25 | 36 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 29 | S/Air High Cutoff TD | 3 |  |  |  | FALSE | No Fault Detected | Default |  | 3 |  | 0 | 10 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 30 | S/Air Low Cutoff TD | 15 |  |  |  | FALSE | No Fault Detected | Default |  | 15 |  | 15 | 30 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 32 | O/Air Clg Enable Stg1 | 78 |  | °F |  | FALSE | No Fault Detected | Default |  | 78 |  | 55 | 85 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 33 | Active O/Air Cool Setpt | 78 |  | °F |  | FALSE | No Fault Detected | 9 | SupplyAirSetpointDFandIFV48aBacNet | 78 |  | 68 | 80 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 34 | System Delta T | 0 |  | °F |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | 0 |  | -58 | 482 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 36 | HGRH S/Air Setpoint | 68 |  | °F |  | FALSE | No Fault Detected | Default |  | 68 |  | 50 | 75 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 37 | Space Pressure Setpoint | 0 |  | in(H2O) |  | FALSE | No Fault Detected | Default |  | 0 |  | -10.047 | 10.047 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 38 | O/Air Dpr Min Position | 100 |  | % |  | FALSE | No Fault Detected | Default |  | 100 |  | 0 | 100 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 39 | S/Air Min Heat Set Point | 45 |  | °F |  | FALSE | No Fault Detected | Default |  | 45 |  | 45 | 90 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | AV | 43 | System Airflow | NaN |  | cfm |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | 0 |  | 0 | 10000 |  |  |  | FALSE | FALSE | FALSE | FALSE | [12 empty] | 0 | 0 | 0 | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BI | 1 | O/Air Damper End Switch | TRUE |  |  | UI4.binaryValue | FALSE | No Fault Detected | [7 empty] | FALSE | FALSE |  |  |  |  | FALSE |  |  | 0 |  |  |  | 0:00 |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BI | 2 | Occupancy Control Input Local | TRUE |  |  | UI5.binaryValue | FALSE | No Fault Detected | [7 empty] | FALSE | FALSE |  |  |  |  | FALSE |  |  | 0 |  |  |  | 0:00 |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BI | 3 | Fan Status Switch Local | TRUE |  |  | UI6.binaryValue | FALSE | No Fault Detected | [7 empty] | FALSE | FALSE |  |  |  |  | FALSE |  |  | 0 |  |  |  | 0:00 |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BI | 4 | Emergency Stop Input | TRUE |  |  | UI7.binaryValue | FALSE | No Fault Detected | [7 empty] | FALSE | FALSE |  |  |  |  | FALSE |  |  | 0 |  |  |  | 0:00 |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 1 | 2-Position OA Damper | FALSE |  |  | BO1 (Relay).binaryValue | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 2 | G - INDOOR FAN | FALSE |  |  | BO2 (Relay).binaryValue | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 3 | Y1 - COOLING | FALSE |  |  | BO3 (Relay).binaryValue | FALSE | No Fault Detected | 9 | DXCoolingControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 4 | Y2 - COOLING | FALSE |  |  | BO4 (triac).binaryValue | FALSE | No Fault Detected | 9 | DXCoolingControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 5 | HOT GAS REHEAT | FALSE |  |  | XM.32.1.BO1 (Relay).binaryValue | FALSE | Unreliable Other | 9 | BurnerControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BO | 6 | W - HEATING | FALSE |  |  | XM.32.1.BO2 (Relay).binaryValue | FALSE | Unreliable Other | 9 | BurnerControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE |  |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | 0:00 | 16 | [6 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 1 | Fan Failure Reset (BAS) | FALSE |  |  |  | TRUE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 2 | Alarm Reset (BAS) | FALSE |  |  |  | TRUE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 3 | Occupancy Input (BAS) | FALSE |  |  |  | TRUE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 4 | Diagnostic: Sensor Failure | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 5 | R/Air Damper | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 6 | Diagnostic: OA Damper Failure | FALSE |  |  |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | TRUE | FALSE | 1 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 7 | S/Air High Temp Cutout | FALSE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 8 | Clg HGRH Duty Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DutyCycleDFandIFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 9 | Alarm Reset | FALSE |  |  |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 10 | Space SP Thumbwheel | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 11 | Heating Failure | FALSE |  |  |  | FALSE | No Fault Detected | 9 | BurnerControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | FALSE | TRUE | FALSE | 2 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 12 | Space Heat/Cool Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 13 | System Lock-Out Alarm | FALSE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 1 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 14 | S/Air Low Temp Cutout | FALSE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 15 | O/Air Cooling Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 16 | O/Air Heating Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 17 | O/Air Ventilation Mode | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 18 | Space Temp Sensor | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 19 | Space RH Sensor | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 20 | Info Alarm Active | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 21 | HGRH Coil | TRUE |  |  |  | FALSE | No Fault Detected | Default |  | TRUE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 22 | Reset Duty Cycle Timer | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DutyCycleDFandIFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 23 | Unoccu Dehumid Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 24 | Cooling Stage 1 Allowed | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 25 | Cooling Stage 2 Allowed | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 26 | Diagnostic: S/A Temp Sensor Failure | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | TRUE | FALSE | 2 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 27 | Diagnostic: O/A Temp Sensor Failure | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 28 | Diagnostic: O/A RH Sensor Failure | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 29 | Setpoint Source | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 30 | Heating is Running | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DutyCycleDFandIFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 31 | Cooling is Running | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DutyCycleDFandIFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 32 | HGRH Purge Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DutyCycleDFandIFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 33 | Alarm Status | TRUE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 34 | O/Air Dehumid Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 35 | Diagnostic: Indoor Fan Failure | FALSE |  |  |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | FALSE | TRUE | FALSE | 1 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 36 | Fan Failure Reset | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 37 | Unocc Cooling Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 38 | Unocc Heating Mode | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 39 | Space Heat Lockout | FALSE |  |  |  | FALSE | No Fault Detected | 9 | ModeandSetpointsDFandIFV48aPart1BacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 40 | Diagnostic: Space Temp Sensor Failure | FALSE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 41 | Diagnostic: Space RH Sensor Failure | FALSE |  |  |  | FALSE | No Fault Detected | 9 | AlarmsDFandIFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | TRUE |  |  |  |  | 0:00 | 0:00 | TRUE | FALSE | FALSE | 3 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 42 | Y2 - Space Lockout | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DXCoolingControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 43 | HGRH Required | TRUE |  |  |  | FALSE | No Fault Detected | 9 | BurnerControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 44 | Space Pressure Used | FALSE |  |  |  | FALSE | No Fault Detected | Default |  | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 45 | OA Damper Enable | FALSE |  |  |  | FALSE | No Fault Detected | 9 | FanControl_20T_DFV48bBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 46 | Y1 - Space Lockout | FALSE |  |  |  | FALSE | No Fault Detected | 9 | DXCoolingControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | BV | 48 | HGRH ON | FALSE |  |  |  | FALSE | No Fault Detected | 9 | BurnerControlDFV48aBacNet | FALSE |  |  |  |  | FALSE | FALSE | [9 empty] | 0:00 | 0:00 |  |  |  | FALSE |  |  |  |  | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE
20T DF v4.8b | 0 | Field Programmable | UC600 | MI | 1 | tov_S/Air Temperature | Idle |  |  | UI1.mode | FALSE | No Fault Detected |  |  |  | [1, Idle] [2, Timed Override Requested] [3, Timed Override Request Cancelled] | [12 empty] | 0 |  |  |  | 0:00 | [7 empty] | 0:00 | 0:00 | FALSE | FALSE | FALSE | 0 | alarm | [11 empty] | FALSE

## RRU-Kitchen direct cookline
|  | 20T DF v4.8b |  | UC600 |  | 08/19/2019 08:34:58
Point Type | Point Instance | Point Name | Shipped Value | Field Change To | Unit | Reference
AV | 8 | S/Air Low Temp Cutoff | 34 |  | °F | SA temp where unit shuts off
AV | 9 | S/Air High Temp Cutoff | 125 |  | °F | SA temp where unit shuts off
AV | 12 | Occ S/Air Heating SP | 72 | 65 | °F | Heat Discharge air temp set point
AV | 15 | Y1 - O/A Dehumid Enable | 28 | 23 | BTU/lb | OA Enthalpy Y1 set point
AV | 16 | Y2 - O/A Dehumid Enable | 36 | 30 | BTU/lb | OA Enthalpy Y2 set point
AV | 20 | O/Air Heating Enable SP | 50 | 55 | °F | OA Heat Set point
AV | 21 | Y1 - O/A Cooling Enable | 78 | 68 | °F | OA Cool Enable
AV | 29 | S/Air High Cutoff TD | 3 | 5 |  | High temp cutoff time delay
AV | 30 | S/Air Low Cutoff TD | 15
AV | 39 | S/Air Min Heat Set Point | 45 | 55 | °F | min heat supply air temp
BV | 21 | HGRH Coil | TRUE | FALSE |  | HGRH is not used
BV | 18 | Space Temp Sensor/Humidity Sensor/Thumbwheel | Not Used | Not Used |  | "Installed" makes unit follow space setpoints
BV | 29 | Setpoint Source | Keypad | SCC |  | Change to SCC

## RRU-Dining to RTUs
|  | 20T DF v4.8b |  | UC600 |  | 08/19/2019 08:34:58
Point Type | Point Instance | Point Name | Shipped Value | Field Change To | Unit | Reference
AV | 8 | S/Air Low Temp Cutoff | 34 | no change | °F | SA temp where unit shuts off
AV | 9 | S/Air High Temp Cutoff | 125 | no change | °F | SA temp where unit shuts off
AV | 12 | Occ S/Air Heating SP | 72 | 65 | °F | Heat Discharge air temp set point
AV | 15 | Y1 - O/A Dehumid Enable | 28 | 28 | BTU/lb | OA Enthalpy Y1 set point
AV | 16 | Y2 - O/A Dehumid Enable | 36 | 32 | BTU/lb | OA Enthalpy Y2 set point
AV | 20 | O/Air Heating Enable SP | 50 | 55 | °F | OA Heat Set point
AV | 21 | Y1 - O/A Cooling Enable | 78 | 68 | °F | OA Cool Enable
AV | 29 | S/Air High Cutoff TD | 3 | 5 |  | High temp cutoff time delay
AV | 30 | S/Air Low Cutoff TD | 15 | no change
AV | 39 | S/Air Min Heat Set Point | 45 | 55 | °F | min heat supply air temp
BV | 21 | HGRH Coil | TRUE | FALSE |  | HGRH is not used
BV | 18 | Space Temp Sensor/Humidity Sensor/Thumbwheel | Not Used | Not Used |  | "Installed" makes unit follow space setpoints
BV | 29 | Setpoint Source | Keypad | SCC |  | Change to SCC

## OAU-Kitchen Direct to Cookline
|  | OAU Points for KITCHEN |  | UC600 |  | 2020-08-05
Point Type | Point Instance | Point Name | Shipped Value | Field Change To | Unit | Reference
AV | 10 | Outdoor Air Dewpoint Setpoint (OADS) |  | 63 | °F | When outdoor dewpoint is above this, unit is in dehum
AV | 14 | Evaporator Leaving Temperature Setpoint |  | 55 | F | During dehum compressors stage to this setpoint
AV | 26 | Unoccupied Cooling Setpoint |  | 80 | F
AV | 27 | Unoccupied Heating Setpoint |  | 65 | F
AV | 28 | Unoccupied Dewpoint Setpoint |  | 65 | F
AV | 29 | Outdoor Air Cooling Setpoint (OACS) |  | 65 | F | When the O/A cooling is above this, unit is in cooling
AV | 30 | Discharge Air Cooling Setpoint |  | 62 | F | Discharge temp controls to this setpoint during cooling
AV | 32 | Discharge Air Heating Setpoint |  | 62 | F | Discharge temp controls to this setpoint during heating
AV | 33 | Outdoor Air Heating Setpoint (OAHS) |  | 55 | F | When the O/A cooling is below this, unit is in heating
AV | 39 | SUPPLY AIRFLOW SETPOINT |  | PUT IN SERVICE
AV | 45 | Maximum Supply Air Temperature |  | PUT IN SERVICE
AV | 47 | Maximum OA Damper Position |  | 100 |  | Max damper position used during economizer mode
AV | 48 | Minimum OA Damper Position |  | 100 |  | Standard position for modulating dampers
AV | 66 | Discharge Air Temperature Setpoint |  | PUT IN SERVICE
AV | 67 | Discharge Air Temperature Setpoint BAS |  | PUT OUT OF SERVICE
BV | 20 | Space Temp/Humidity Sensor Installed |  | Not Installed |  | Disables unoccupied cool/heat/dehum
MV | 13 | System Control Type |  | Discharge Air Control |  | Puts unit in space or discharge air control

## OAU-Dining to RTUs
|  | OAU Points for Dining/RTUS |  | UC600 |  | 2020-08-05
Point Type | Point Instance | Point Name | Shipped Value | Field Change To | Unit | Reference
AV | 10 | Outdoor Air Dewpoint Setpoint (OADS) |  | 60 | °F | When outdoor dewpoint is above this, unit is in dehum
AV | 14 | Evaporator Leaving Temperature Setpoint |  | 55 | F | During dehum compressors stage to this setpoint
AV | 29 | Outdoor Air Cooling Setpoint (OACS) |  | 80 | F | When the O/A cooling is above this, unit is in cooling
AV | 30 | Discharge Air Cooling Setpoint |  | 70 | F | Discharge temp controls to this setpoint during cooling
AV | 32 | Discharge Air Heating Setpoint |  | 68 | F | Discharge temp controls to this setpoint during heating
AV | 33 | Outdoor Air Heating Setpoint (OAHS) |  | 50 | F | When the O/A cooling is below this, unit is in heating
AV | 39 | SUPPLY AIRFLOW SETPOINT |  | PUT IN SERVICE
AV | 45 | Maximum Supply Air Temperature |  | PUT IN SERVICE
AV | 47 | Maximum OA Damper Position |  | 100 |  | Max damper position used during economizer mode
AV | 48 | Minimum OA Damper Position |  | 100 |  | Standard position for modulating dampers
AV | 66 | Discharge Air Temperature Setpoint Active |  | PUT IN SERVICE
AV | 67 | Discharge Air Temperature Setpoint BAS |  | PUT OUT OF SERVICE
BV | 20 | Space Temp/Humidity Sensor Installed |  | Not Installed |  | Disables unoccupied cool/heat/dehum
MV | 13 | System Control Type |  | Discharge Air Control |  | Puts unit in space or discharge air control